HWP No. ______________

HOT OR OPEN FLAME WORK – Procedure

- Background

Hot work is defined as any work process in which a flame is used or sparks or other sources of ignition may be produced, including:

- open flames ie cutting, welding, burning

- electrical, friction or impact sparks ie. Air gouging, riveting, drilling, grinding, chipping

The purpose of this procedure is to establish procedures for safe hot or open flame work in specific campus locations. Compliance with this policy is the responsibility of the appropriate supervisor and the workers carrying out the procedure. EXCLUSION: This policy does not apply to shop areas which are designed for this type of work (e.g. welding shop, trades shops).

2.0   Procedure

A University of Ottawa Hot Work Permit is attached to this SOP and is to be completed whenever hot work is being carried out. The checklist on the form covers the topics below and assists the individual or contractor in taking the necessary precautions. The completed form is to be attached to the completed work order or the confined space entry permit as applicable.

- Prior to the work commencing, the Physical Resources Lead hand, Supervisors or Project Managers will issue and approve the Hot Work permit.  Other Services and Departments may issue permits under the authority of the Office of Risk Management or the Fire Safety Officer.  The initial request for the Permit should be initiated 48 hours before work is to be commenced. The permit will indicate:

i)   that hot or open flame work is to be carried out.
ii)   the specific location where the work is being done.
iii)   confirm that fire extinguisher is on site.
iv)   indicate whether or not a smoke/heat detector has been deactivated or a zone deactivated.
v)   when the work will commence and the expected time of it completion.

- The person reviewing the Hot Works Procedure and requirements with the person(s) responsible for the work will sign the form. This could initially be the Project Manager, but could also include the General Contractor  responsible for reviewing the procedure with his workers/subcontractors. Although only one Hot Works permit is required per project, many projects last several weeks, and a  Firewatch will have to be completed for every day where Hot Works procedures are carried out during that project.

- A copy of the permit will be faxed to the University Fire Safety Officer (613-562-5183). Alternatively, the completed form can also be scanned and sent by E-mail to Marc Denis at marc.denis@uOttawa.ca

- If applicable, the issuer should inform occupants who work in the proximity of the work area prior to work commencing. This communication should be directed to the proper building manager. Signage should also be installed near the work area prior to work commencing. Both these measures will ensure that fire alarms are not needlessly activated.

- Check the area for the proximity of heat or smoke detectors. If there is the possibility these may accidentally be triggered, the worker is to arrange with a Physical Resources electrician at least 48 hours in advance, to deactivate the zone or the detector.

- Upon arrival at the work location, ensure that all flammable materials, where practical, are removed from the area where the work will be carried out. Where this is not practical, isolate the material with a fireproof barrier.

- No work shall be done unless a 5 lb (ABC) dry chemical fire extinguisher is on hand. The worker shall locate where the nearest fire alarm pull station is.

- A Fire Watch is to be conducted during and for 60 minutes after the hot work is complete to ensure that there are no hot spots, smoke or other indications of a possible fire in the area around the work site. The contractor assumes the role of firewatch if he is working alone. The firewatch person is not to leave the area during this period, however other work may be carried out as long as the area in question is in full view.

- After this initial 1 hour watch, the firewatch is to continue for an additional hour, however the worker can leave the area as long as he returns to complete the Firewatch.. The total Firewatch period is therefore 2 hours duration after completion of the work.

- The Physical Resources electrician is to be notified that the zone or smoke/heat detector needs to be reactivated if required.

- The worker will depart from the site removing all work materials and debris, sign off on fire watch on the  permit and return the completed form to the Protection desk (141 Louis-Pasteur), c/o Fire Safety Officer. If work is to be conducted at Roger Guindon or 200 Lees, the form can also be returned to the respective Protection desk , c/o Fire Safety Officer ( Marc Denis).

- The Fire Safety Officer will conduct random inspections as deemed necessary